## Appendix I
Appendix I Wind turbine power performance curves
I1 Free-Standing Mast-Mounted Wind Turbine
I2. Mark 1 Aeolian Roof Wind Turbine
Figure I.1. Position of the Aeolian Roof Wind Turbine in the Silsoe Structures Building. Units:m.
Figure I.2. Detail of the position of the wind turbine relative to the building ridge. Mark 1 Aeolian Roof. Units: m.
Vi average wind speed in bin i, in m/s
Pi average wind turbine power output in bin i, in W
RPM average wind turbine rotational speed in bin i, in revolutions per minute
Ni number of 1-minute data sets in bin i
si statistical uncertainty of the normalized and averaged power in bin i
ui uncertainty in bin i related to the instruments used for the measurements
uci combined uncertainty of the wind turbine power output in bin i

## I1
Back to Appendix I |  | I.1 Free-Standing Mast-Mounted Wind Turbine
Wind turbine | MMWT | [6 empty] | MMWT Fixed-Yaw
diameter=0.91m | free-yaw | [6 empty] | wind directions 0-5deg of the building transverse wind direction | [6 empty] | wind directions 5-15deg of the building transverse wind direction | [6 empty] | wind directions 15-25deg of the building transverse wind direction | [6 empty] | wind directions 25-35deg of the building transverse wind direction | [6 empty] | wind directions 35-45deg of the building transverse wind direction | [6 empty] | wind directions 45-55deg of the building transverse wind direction | [6 empty] | wind directions 55-65deg of the building transverse wind direction | [6 empty] | wind directions 65-75deg of the building transverse wind direction | [6 empty] | wind directions 75-90deg of the building transverse wind direction
| m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power)
Bin i in m/s | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci
[0.25-0.75] | 0.52 | 0 | 1.6 | 76 | 0 | 0 | 0 | 0.74 | 0 | 1.8 | 1 | N/A | N/A | N/A | 0.45 | 0 | 1.8 | 1 | N/A | N/A | N/A | 0.53 | 0 | 9.72 | 5 | 0 | 0 | 0 | 0.53 | 0 | 1.9 | 2 | 0 | 0 | 0 | 0.52 | 0 | 1.9 | 2 | 0 | 0 | 0 | 0.65 | 0 | 1.9 | 3 | 0 | 0 | 0 | 0.54 | 0 | 1.9 | 3 | 0 | 0 | 0 | 0.47 | 0 | 1.87 | 3 | 0 | 0 | 0 | 0.38 | 0 | 1.87 | 3 | 0 | 0 | 0
[0.75-1.25] | 0.98 | 0 | 22.48 | 18 | 0 | 0 | 0 | 1.01 | 0 | 33.53 | 6 | 0 | 0 | 0 | 1.04 | 0 | 26 | 6 | 0 | 0 | 0 | 0.98 | 0 | 8.52 | 5 | 0 | 0 | 0 | 0.94 | 0 | 10.28 | 4 | 0 | 0 | 0 | 1.15 | 0 | 13.56 | 5 | 0 | 0 | 0 | 0.86 | 0 | 3.77 | 6 | 0 | 0 | 0 | 1.04 | 0 | 3 | 6 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[1.25-1.75] | 1.57 | 0.05 | 61.19 | 54 | 0 | 0.01 | 0.01 | 1.63 | 0.04 | 61.94 | 7 | 0 | 0.01 | 0.01 | 1.58 | 0.03 | 57.99 | 11 | 0.01 | 0.01 | 0.01 | 1.65 | 0.03 | 50.95 | 23 | 0 | 0.01 | 0.01 | 1.53 | 0.01 | 39.99 | 23 | 0 | 0 | 0.01 | 1.61 | 0.01 | 40.37 | 19 | 0 | 0 | 0 | 1.51 | 0 | 23.37 | 11 | 0 | 0 | 0 | 1.61 | 0 | 12.56 | 12 | 0 | 0 | 0 | 1.62 | 0 | 15.65 | 2 | N/A | N/A | N/A | 1.62 | 0 | 1.9 | 6 | N/A | N/A | N/A
[1.75-2.25] | 2 | 0.19 | 91.25 | 88 | 0.02 | 0.02 | 0.03 | 2.1 | 0.2 | 97.31 | 10 | 0.03 | 0.03 | 0.04 | 1.99 | 0.15 | 84.11 | 16 | 0.03 | 0.03 | 0.04 | 2.01 | 0.1 | 73.42 | 40 | 0.01 | 0.02 | 0.02 | 2 | 0.08 | 66.78 | 60 | 0.01 | 0.02 | 0.02 | 2.02 | 0.05 | 58.92 | 52 | 0.01 | 0.01 | 0.01 | 2.03 | 0.02 | 46.16 | 27 | 0 | 0.01 | 0.01 | 2.04 | 0.01 | 34.01 | 12 | 0 | 0 | 0.01 | 1.95 | 0 | 4.38 | 6 | 0 | 0 | 0 | 2.04 | 0 | 2.41 | 16 | 0 | 0 | 0
[2.25-2.75] | 2.55 | 0.89 | 153.42 | 109 | 0.04 | 0.06 | 0.07 | 2.49 | 0.62 | 144.38 | 14 | 0.07 | 0.09 | 0.11 | 2.51 | 0.53 | 131.34 | 28 | 0.06 | 0.07 | 0.09 | 2.51 | 0.48 | 121.77 | 51 | 0.04 | 0.07 | 0.08 | 2.5 | 0.31 | 102.69 | 85 | 0.02 | 0.05 | 0.05 | 2.53 | 0.19 | 89.42 | 92 | 0.01 | 0.03 | 0.03 | 2.57 | 0.11 | 74.01 | 37 | 0.01 | 0.02 | 0.02 | 2.53 | 0.01 | 41.64 | 17 | 0 | 0.01 | 0.01 | 2.51 | 0 | 22.41 | 33 | 0 | 0 | 0 | 2.55 | 0 | 10.73 | 53 | 0 | 0 | 0
[2.75-3.25] | 3.03 | 1.86 | 206.98 | 127 | 0.05 | 0.1 | 0.11 | 3.03 | 1.85 | 223.72 | 17 | 0.09 | 0.23 | 0.25 | 3.04 | 1.72 | 214.75 | 50 | 0.05 | 0.23 | 0.23 | 3.01 | 1.18 | 177.27 | 83 | 0.05 | 0.15 | 0.16 | 3.01 | 0.89 | 156.15 | 97 | 0.04 | 0.12 | 0.13 | 3 | 0.45 | 120.95 | 137 | 0.02 | 0.06 | 0.07 | 3.01 | 0.21 | 92.76 | 77 | 0.02 | 0.03 | 0.04 | 2.99 | 0.07 | 70.12 | 36 | 0.01 | 0.02 | 0.02 | 3.03 | 0.01 | 44.36 | 55 | 0 | 0.01 | 0.01 | 3.01 | 0 | 13.07 | 88 | 0 | 0 | 0
[3.25-3.75] | 3.53 | 3.17 | 260.71 | 173 | 0.05 | 0.15 | 0.15 | 3.49 | 2.89 | 268.53 | 30 | 0.09 | 0.27 | 0.28 | 3.52 | 2.8 | 264.53 | 109 | 0.05 | 0.27 | 0.28 | 3.51 | 2.45 | 247.65 | 113 | 0.05 | 0.29 | 0.3 | 3.5 | 1.83 | 216.56 | 112 | 0.06 | 0.22 | 0.23 | 3.47 | 0.93 | 160.63 | 136 | 0.04 | 0.12 | 0.13 | 3.5 | 0.42 | 116.91 | 82 | 0.03 | 0.06 | 0.06 | 3.47 | 0.14 | 88.17 | 31 | 0.01 | 0.02 | 0.03 | 3.49 | 0.04 | 63.82 | 77 | 0 | 0.01 | 0.01 | 3.49 | 0 | 22.43 | 79 | 0 | 0 | 0
[3.75-4.25] | 4.01 | 4.73 | 310.79 | 231 | 0.05 | 0.21 | 0.21 | 3.99 | 4.43 | 320.57 | 42 | 0.12 | 0.41 | 0.43 | 4.01 | 4.28 | 317.05 | 125 | 0.05 | 0.4 | 0.41 | 4 | 3.84 | 301.22 | 127 | 0.06 | 0.38 | 0.38 | 3.98 | 3.07 | 275.9 | 86 | 0.07 | 0.34 | 0.35 | 3.98 | 1.7 | 206.45 | 87 | 0.08 | 0.21 | 0.22 | 3.99 | 0.97 | 161.9 | 66 | 0.07 | 0.15 | 0.17 | 4.02 | 0.42 | 124.61 | 62 | 0.04 | 0.07 | 0.08 | 3.98 | 0.09 | 77.75 | 53 | 0.01 | 0.02 | 0.02 | 4.02 | 0.01 | 37.51 | 57 | 0 | 0.01 | 0.01
[4.25-4.75] | 4.52 | 6.68 | 361.94 | 285 | 0.05 | 0.28 | 0.28 | 4.49 | 6.56 | 380.36 | 47 | 0.15 | 0.63 | 0.64 | 4.53 | 6.24 | 371.23 | 107 | 0.09 | 0.57 | 0.58 | 4.48 | 5.61 | 354.26 | 115 | 0.08 | 0.55 | 0.55 | 4.48 | 4.62 | 328.53 | 66 | 0.11 | 0.46 | 0.47 | 4.5 | 3.1 | 271.55 | 80 | 0.11 | 0.4 | 0.41 | 4.47 | 1.55 | 198.71 | 54 | 0.11 | 0.18 | 0.21 | 4.47 | 0.78 | 158.71 | 63 | 0.05 | 0.12 | 0.13 | 4.55 | 0.2 | 92.36 | 56 | 0.02 | 0.03 | 0.04 | 4.51 | 0.02 | 45.26 | 52 | 0 | 0.01 | 0.01
[4.75-5.25] | 5 | 9.07 | 413.83 | 257 | 0.06 | 0.37 | 0.37 | 5.02 | 9.21 | 440 | 46 | 0.2 | 0.83 | 0.86 | 5 | 8.64 | 426.46 | 95 | 0.11 | 0.84 | 0.84 | 4.98 | 7.75 | 408.67 | 78 | 0.11 | 0.71 | 0.72 | 4.99 | 6.45 | 383.36 | 55 | 0.16 | 0.6 | 0.62 | 5.02 | 4.89 | 332.61 | 48 | 0.16 | 0.56 | 0.58 | 4.95 | 2.85 | 261.74 | 43 | 0.18 | 0.44 | 0.47 | 4.98 | 1.47 | 200.11 | 48 | 0.12 | 0.22 | 0.25 | 4.97 | 0.41 | 119.06 | 38 | 0.04 | 0.09 | 0.09 | 4.94 | 0.04 | 55.89 | 29 | 0.01 | 0.01 | 0.01
[5.25-5.75] | 5.48 | 11.97 | 467.56 | 195 | 0.09 | 0.48 | 0.49 | 5.49 | 12.16 | 497.78 | 52 | 0.17 | 1.13 | 1.14 | 5.51 | 11.81 | 491.92 | 96 | 0.16 | 1.12 | 1.13 | 5.5 | 10.76 | 473.13 | 70 | 0.19 | 1.03 | 1.05 | 5.52 | 9.07 | 442 | 42 | 0.25 | 0.89 | 0.92 | 5.49 | 7.11 | 396.24 | 54 | 0.2 | 0.84 | 0.87 | 5.47 | 3.63 | 289.98 | 22 | 0.31 | 0.29 | 0.42 | 5.5 | 2.23 | 240.33 | 35 | 0.14 | 0.27 | 0.3 | 5.49 | 0.69 | 144.11 | 30 | 0.09 | 0.1 | 0.13 | 5.45 | 0.11 | 68.52 | 17 | 0.04 | 0.03 | 0.04
[5.75-6.25] | 5.99 | 15.58 | 526.26 | 173 | 0.11 | 0.61 | 0.62 | 6 | 15.56 | 555.36 | 62 | 0.16 | 1.31 | 1.31 | 5.99 | 15.1 | 549.9 | 117 | 0.15 | 1.34 | 1.35 | 6.02 | 13.93 | 534.34 | 60 | 0.24 | 1.21 | 1.23 | 6.01 | 11.47 | 487.47 | 30 | 0.27 | 0.97 | 1.01 | 6.02 | 9.45 | 448.82 | 40 | 0.27 | 0.88 | 0.92 | 6.01 | 6.96 | 396.12 | 23 | 0.38 | 1.18 | 1.24 | 6.01 | 3.67 | 300.24 | 40 | 0.21 | 0.55 | 0.59 | 6.01 | 1.04 | 174.5 | 23 | 0.14 | 0.14 | 0.2 | 6.03 | 0.15 | 80.13 | 13 | 0.03 | 0.02 | 0.04
[6.25-6.75] | 6.5 | 19.86 | 590.79 | 128 | 0.16 | 0.77 | 0.79 | 6.52 | 20.04 | 626.57 | 83 | 0.23 | 1.82 | 1.84 | 6.5 | 19.35 | 616.91 | 112 | 0.17 | 1.76 | 1.77 | 6.48 | 17.52 | 588.69 | 59 | 0.22 | 1.64 | 1.65 | 6.51 | 15.17 | 552.52 | 29 | 0.34 | 1.56 | 1.6 | 6.48 | 11.45 | 487.57 | 22 | 0.51 | 0.93 | 1.06 | 6.49 | 9.73 | 464.68 | 29 | 0.35 | 1.22 | 1.27 | 6.54 | 4.29 | 322.6 | 29 | 0.28 | 0.28 | 0.39 | 6.52 | 1.52 | 204.13 | 31 | 0.14 | 0.2 | 0.25 | 6.54 | 0.2 | 94.45 | 14 | 0.02 | 0.03 | 0.04
[6.75-7.25] | 7 | 24.41 | 652.58 | 77 | 0.21 | 0.94 | 0.97 | 6.99 | 24.01 | 679.11 | 80 | 0.22 | 1.98 | 1.99 | 7.01 | 24.03 | 678.33 | 128 | 0.19 | 2.11 | 2.12 | 6.97 | 22.07 | 654.6 | 67 | 0.24 | 2.11 | 2.12 | 6.98 | 19.82 | 621.49 | 25 | 0.58 | 2.27 | 2.34 | 6.98 | 14.69 | 543.17 | 10 | 0.72 | 1.49 | 1.65 | 6.98 | 11.57 | 501.79 | 11 | 0.72 | 0.87 | 1.13 | 6.99 | 5.38 | 351.08 | 34 | 0.38 | 0.55 | 0.67 | 6.97 | 1.8 | 219.66 | 38 | 0.15 | 0.16 | 0.22 | 7.03 | 0.32 | 107.09 | 19 | 0.06 | 0.06 | 0.09
[7.25-7.75] | 7.48 | 29.65 | 717.45 | 81 | 0.31 | 1.14 | 1.18 | 7.53 | 29.72 | 749.12 | 63 | 0.26 | 2.6 | 2.61 | 7.52 | 29.11 | 742.63 | 115 | 0.23 | 2.45 | 2.46 | 7.48 | 26.75 | 718.41 | 63 | 0.37 | 2.24 | 2.27 | 7.52 | 23.42 | 668.39 | 28 | 0.54 | 1.66 | 1.75 | 7.45 | 18.07 | 598.91 | 15 | 0.78 | 1.75 | 1.91 | 7.45 | 14.01 | 543.34 | 24 | 0.52 | 1.27 | 1.37 | 7.48 | 7.78 | 416.19 | 32 | 0.46 | 1.18 | 1.27 | 7.49 | 2.39 | 246.8 | 36 | 0.19 | 0.29 | 0.35 | 7.51 | 0.36 | 110.58 | 23 | 0.06 | 0.03 | 0.07
[7.75-8.25] | 8.01 | 35.65 | 782.09 | 86 | 0.29 | 1.36 | 1.39 | 8.02 | 35.68 | 814.13 | 50 | 0.4 | 3.17 | 3.19 | 7.97 | 34.16 | 800.18 | 86 | 0.28 | 2.92 | 2.93 | 8.02 | 33.12 | 791 | 49 | 0.39 | 3.11 | 3.13 | 8.04 | 27.66 | 722.24 | 18 | 0.67 | 2.15 | 2.25 | 7.93 | 21.53 | 644.56 | 8 | 1.17 | 1.85 | 2.19 | 8.01 | 18.04 | 611.26 | 14 | 0.55 | 1.87 | 1.95 | 7.95 | 8.42 | 429.66 | 12 | 0.83 | 0.4 | 0.92 | 7.97 | 2.89 | 259.99 | 25 | 0.36 | 0.28 | 0.46 | 7.96 | 0.49 | 124.92 | 27 | 0.07 | 0.08 | 0.11
[8.25-8.75] | 8.23 | 38.77 | 812.88 | 95 | 0.31 | 1.48 | 1.51 | 8.47 | 41.27 | 871.61 | 36 | 0.45 | 3.4 | 3.43 | 8.49 | 41.17 | 873.67 | 56 | 0.33 | 3.72 | 3.73 | 8.48 | 38.74 | 850.2 | 29 | 0.61 | 3.37 | 3.42 | 8.49 | 34.23 | 796.62 | 16 | 0.81 | 3.96 | 4.04 | 8.45 | 23.26 | 666.9 | 5 | 1.76 | 1.03 | 2.04 | 8.49 | 20.32 | 634.1 | 4 | 3.03 | 1.35 | 3.32 | 8.43 | 11.63 | 497.11 | 14 | 0.86 | 1.82 | 2.01 | 8.49 | 3.91 | 301.51 | 12 | 0.5 | 0.54 | 0.73 | 8.45 | 0.63 | 142.45 | 23 | 0.1 | 0.08 | 0.13
[8.75-9.25] | 8.76 | 45.96 | 881.7 | 64 | 0.43 | 1.75 | 1.8 | 9.03 | 49.27 | 948.49 | 19 | 0.82 | 4.27 | 4.35 | 9.01 | 49.32 | 952.7 | 40 | 0.67 | 4.57 | 4.62 | 9 | 46.69 | 927.55 | 23 | 0.69 | 4.45 | 4.5 | 8.99 | 38.81 | 834.03 | 9 | 1.24 | 2.74 | 3.01 | 8.98 | 31.9 | 774.12 | 5 | 1.8 | 4.65 | 4.98 | 9.13 | 25.6 | 698.55 | 2 | 2.34 | 2.44 | 3.38 | 8.98 | 13.84 | 536.38 | 11 | 1.11 | 1.18 | 1.62 | 8.96 | 5.73 | 347.88 | 6 | 1.41 | 1.11 | 1.8 | 8.88 | 0.35 | 113.46 | 12 | 0.07 | 0.19 | 0.21
[9.25-9.75] | 9.23 | 52.39 | 937.37 | 75 | 0.41 | 1.99 | 2.03 | 9.46 | 58.09 | 1024.46 | 13 | 0.66 | 6.18 | 6.22 | 9.48 | 56.18 | 1014.01 | 20 | 0.91 | 4.61 | 4.7 | 9.38 | 51.09 | 966.83 | 9 | 1.26 | 3.58 | 3.8 | 9.45 | 46.22 | 907.97 | 6 | 0.97 | 4.97 | 5.06 | 9.5 | 37.58 | 822.38 | 5 | 1.41 | 3.41 | 3.69 | 9.26 | 33.68 | 803.6 | 1 | N/A | N/A | N/A | 9.48 | 11.62 | 496.35 | 2 | 1.65 | 1.35 | 2.13 | 9.44 | 5.27 | 343.13 | 4 | 1.28 | 0.33 | 1.32 | 9.4 | 0.66 | 126.68 | 4 | 0.32 | 0.18 | 0.37
[9.75-10.25] | 9.76 | 62.39 | 1018.09 | 61 | 0.52 | 2.36 | 2.42 | 10 | 68.01 | 1097.77 | 11 | 1.36 | 18.53 | 18.58 | 9.95 | 65.67 | 1097.37 | 22 | 0.68 | 6.48 | 6.52 | 9.99 | 61.36 | 1061.12 | 9 | 1.09 | 5.48 | 5.59 | 10.07 | 57.33 | 1000.85 | 2 | 0.21 | 5.84 | 5.85 | 9.86 | 46.31 | 900.05 | 2 | 0.18 | 7.62 | 7.63 | 9.78 | 37.43 | 846.5 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 9.8 | 2.94 | 266.7 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[10.25-10.75] | 10.22 | 70.9 | 1081.07 | 67 | 0.5 | 2.68 | 2.73 | 10.47 | 76.55 | 1172.24 | 5 | 1.46 | 6.21 | 6.38 | 10.49 | 76.85 | 1171.01 | 19 | 0.82 | 6.96 | 7.01 | 10.54 | 73.96 | 1167.35 | 6 | 1.29 | 7.86 | 7.96 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[10.75-11.25] | 10.76 | 80.39 | 1145.58 | 34 | 0.72 | 3.04 | 3.12 | 11.07 | 89.32 | 1261.98 | 6 | 1.44 | 7.62 | 7.75 | 10.94 | 84.83 | 1242.23 | 4 | 3.2 | 6.44 | 7.19 | 10.92 | 76.11 | 1171 | 3 | 2.4 | 2.51 | 3.48 | 11.08 | 87.11 | 1221.9 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[11.25-11.75] | 11.27 | 92.62 | 1227.44 | 22 | 1.07 | 3.5 | 3.66 | 11.43 | 97.85 | 1317.19 | 7 | 1.66 | 8.97 | 9.12 | 11.47 | 94.4 | 1298.75 | 4 | 1.82 | 6.89 | 7.13 | 11.3 | 88.8 | 1263.1 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[11.75-12.25] | 11.79 | 103.34 | 1294.85 | 22 | 1.58 | 3.9 | 4.2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 11.87 | 108.8 | 1395.8 | 3 | 3.14 | 13.53 | 13.89 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[12.25-12.75] | 12.26 | 112.23 | 1348 | 9 | 1.97 | 4.23 | 4.67 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 12.4 | 120.3 | 1470.5 | 2 | 6.44 | 8.86 | 10.96 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[12.75-13.25] | 12.92 | 129.61 | 1454.03 | 2 | 1.59 | 4.88 | 5.13 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[13.25-13.75] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 13.35 | 133.7 | 1536.5 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[13.75-14.25] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[14.25-14.75] | 14.03 | 158.61 | 1596.03 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Vi | average wind speed in bin i, in m/s
Pi | average wind turbine power output in bin i, in W
RPM | average wind turbine rotational speed in bin i, in revolutions per minute
Ni | number of 1-minute data sets in bin i
si | statistical uncertainty of the normalized and averaged power in bin i
ui | uncertainty in bin i related to the instruments used for the measurements
uci | combined uncertainty of the wind turbine power output in bin i

## I2
Back to Appendix H |  | I.2. Mark 1 Aeolian Roof Wind Turbine
Wind turbine | MMWT | [6 empty] | Mark 1 ARWT
diameter=0.91m | free-yaw | [6 empty] | wind directions 0-5deg of the building transverse wind direction | [6 empty] | wind directions 5-15deg of the building transverse wind direction | [6 empty] | wind directions 15-25deg of the building transverse wind direction | [6 empty] | wind directions 25-35deg of the building transverse wind direction | [6 empty] | wind directions 35-45deg of the building transverse wind direction | [6 empty] | wind directions 45-55deg of the building transverse wind direction | [6 empty] | wind directions 55-65deg of the building transverse wind direction | [6 empty] | wind directions 65-75deg of the building transverse wind direction | [6 empty] | wind directions 75-90deg of the building transverse wind direction
| m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power) |  |  | m/s | W | RPM | Data Num | uncertainties (in power)
Bin i in m/s | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci | Vi | Pi |  | Ni | si | ui | uci
[0.25-0.75] | 0.52 | 0 | 1.6 | 76 | 0 | 0 | 0 | 0.46 | 0 | 6.81 | 12 | 0 | 0 | 0 | 0.5 | 0 | 4.62 | 29 | 0 | 0 | 0 | 0.49 | 0 | 7.4 | 32 | 0 | 0 | 0 | 0.55 | 0 | 4.52 | 26 | 0 | 0 | 0 | 0.56 | 0 | 2.46 | 14 | 0 | 0 | 0 | 0.55 | 0 | 2.12 | 25 | 0 | 0 | 0 | 0.63 | 0 | 7.49 | 10 | 0 | 0 | 0 | 0.57 | 0 | 1.8 | 8 | 0 | 0 | 0 | 0.5 | 0 | 1.8 | 5 | 0 | 0 | 0
[0.75-1.25] | 0.98 | 0 | 22.48 | 18 | 0 | 0 | 0 | 1.05 | 0.01 | 35.26 | 57 | 0 | 0 | 0 | 0.98 | 0.03 | 36.92 | 42 | 0.01 | 0 | 0.01 | 1.02 | 0.01 | 37.48 | 26 | 0.01 | 0 | 0.01 | 0.99 | 0.03 | 46.15 | 27 | 0.02 | 0.01 | 0.02 | 1.06 | 0.01 | 41.22 | 39 | 0 | 0 | 0.01 | 0.99 | 0.01 | 28.66 | 28 | 0 | 0 | 0.01 | 1.06 | 0 | 12.9 | 11 | 0 | 0 | 0 | 0.92 | 0 | 2.21 | 7 | 0 | 0 | 0 | 1.02 | 0.01 | 15.7 | 5 | 0.01 | 0 | 0.01
[1.25-1.75] | 1.57 | 0.05 | 61.19 | 54 | 0 | 0.01 | 0.01 | 1.55 | 0.17 | 70.42 | 25 | 0.05 | 0.02 | 0.06 | 1.51 | 0.24 | 87.3 | 53 | 0.04 | 0.03 | 0.05 | 1.51 | 0.2 | 79.7 | 50 | 0.04 | 0.02 | 0.05 | 1.51 | 0.3 | 81.5 | 37 | 0.17 | 0.03 | 0.17 | 1.52 | 0.26 | 82.61 | 31 | 0.07 | 0.03 | 0.08 | 1.5 | 0.19 | 73.55 | 27 | 0.05 | 0.02 | 0.06 | 1.57 | 0.15 | 64.91 | 8 | 0.11 | 0.02 | 0.11 | 1.52 | 0.02 | 23.55 | 4 | 0.02 | 0 | 0.02 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[1.75-2.25] | 2 | 0.19 | 91.25 | 88 | 0.02 | 0.02 | 0.03 | 2.06 | 0.7 | 136.1 | 87 | 0.07 | 0.08 | 0.11 | 2.06 | 0.88 | 147.81 | 140 | 0.07 | 0.09 | 0.11 | 2.03 | 0.62 | 122.44 | 84 | 0.09 | 0.06 | 0.11 | 2.03 | 0.95 | 138.94 | 60 | 0.2 | 0.09 | 0.22 | 2.05 | 1.43 | 178.76 | 59 | 0.18 | 0.16 | 0.24 | 2 | 0.95 | 144.48 | 44 | 0.18 | 0.11 | 0.21 | 2.01 | 0.32 | 95.44 | 14 | 0.09 | 0.03 | 0.1 | 1.96 | 0.1 | 41.05 | 6 | 0.07 | 0.01 | 0.07 | 2.04 | 0 | 7.62 | 11 | N/A | N/A | N/A
[2.25-2.75] | 2.55 | 0.89 | 153.42 | 109 | 0.04 | 0.06 | 0.07 | 2.51 | 1.39 | 182.18 | 158 | 0.09 | 0.14 | 0.16 | 2.52 | 1.54 | 187.56 | 277 | 0.07 | 0.13 | 0.15 | 2.5 | 1.22 | 166.94 | 132 | 0.09 | 0.11 | 0.15 | 2.53 | 1.61 | 183.4 | 97 | 0.17 | 0.12 | 0.21 | 2.5 | 2.47 | 229.83 | 76 | 0.23 | 0.2 | 0.3 | 2.52 | 2.26 | 211.48 | 74 | 0.25 | 0.22 | 0.33 | 2.57 | 1.24 | 163.53 | 24 | 0.25 | 0.14 | 0.29 | 2.49 | 0.11 | 56.03 | 10 | 0.06 | 0.01 | 0.06 | 2.56 | 0 | 11.02 | 6 | 0 | 0 | 0
[2.75-3.25] | 3.03 | 1.86 | 206.98 | 127 | 0.05 | 0.1 | 0.11 | 3.01 | 2.53 | 236.64 | 187 | 0.12 | 0.23 | 0.26 | 3.01 | 2.47 | 233.78 | 296 | 0.09 | 0.2 | 0.22 | 3.02 | 2.3 | 218.62 | 245 | 0.13 | 0.22 | 0.25 | 3.01 | 2.64 | 229.6 | 134 | 0.21 | 0.22 | 0.3 | 3.03 | 3.9 | 283.24 | 102 | 0.27 | 0.28 | 0.39 | 2.99 | 2.93 | 242.19 | 101 | 0.25 | 0.17 | 0.3 | 2.96 | 1.39 | 170.16 | 36 | 0.23 | 0.07 | 0.24 | 3.01 | 0.25 | 75.27 | 9 | 0.16 | 0.03 | 0.17 | 3.03 | 0.03 | 42.28 | 5 | 0.01 | 0.01 | 0.02
[3.25-3.75] | 3.53 | 3.17 | 260.71 | 173 | 0.05 | 0.15 | 0.15 | 3.5 | 4.14 | 296.34 | 212 | 0.15 | 0.39 | 0.41 | 3.51 | 3.87 | 286.17 | 296 | 0.13 | 0.34 | 0.36 | 3.5 | 3.68 | 273.35 | 270 | 0.16 | 0.34 | 0.37 | 3.5 | 4.29 | 290.06 | 178 | 0.24 | 0.39 | 0.46 | 3.5 | 6.35 | 354.04 | 132 | 0.35 | 0.61 | 0.7 | 3.53 | 5.4 | 329.57 | 99 | 0.33 | 0.53 | 0.62 | 3.5 | 1.91 | 202.85 | 49 | 0.21 | 0.13 | 0.24 | 3.53 | 0.94 | 136.73 | 14 | 0.29 | 0.16 | 0.33 | 3.56 | 0.2 | 76.5 | 4 | 0.12 | 0.04 | 0.13
[3.75-4.25] | 4.01 | 4.73 | 310.79 | 231 | 0.05 | 0.21 | 0.21 | 4.01 | 5.58 | 342.2 | 250 | 0.15 | 0.39 | 0.42 | 4 | 5.7 | 344.28 | 296 | 0.15 | 0.5 | 0.52 | 4.01 | 5.77 | 342.51 | 282 | 0.18 | 0.55 | 0.58 | 3.98 | 5.57 | 330.53 | 129 | 0.29 | 0.37 | 0.47 | 4.01 | 8.43 | 408.69 | 132 | 0.38 | 0.55 | 0.67 | 4 | 7.07 | 368.17 | 108 | 0.41 | 0.49 | 0.63 | 4 | 3.62 | 262.93 | 43 | 0.45 | 0.45 | 0.63 | 4.08 | 0.81 | 144.52 | 10 | 0.16 | 0.05 | 0.17 | 3.92 | 0.01 | 26.3 | 2 | 0.01 | 0.06 | 0.06
[4.25-4.75] | 4.52 | 6.68 | 361.94 | 285 | 0.05 | 0.28 | 0.28 | 4.49 | 7.92 | 400.61 | 215 | 0.23 | 0.73 | 0.76 | 4.49 | 7.79 | 397.13 | 296 | 0.18 | 0.63 | 0.66 | 4.5 | 8.17 | 406.45 | 208 | 0.24 | 0.72 | 0.76 | 4.52 | 9.05 | 424.47 | 134 | 0.34 | 0.95 | 1.01 | 4.5 | 10.41 | 448.42 | 120 | 0.51 | 0.63 | 0.81 | 4.5 | 9.72 | 435.33 | 110 | 0.43 | 0.8 | 0.9 | 4.5 | 5.57 | 319.62 | 28 | 0.86 | 0.58 | 1.04 | 4.46 | 0.63 | 131.97 | 9 | 0.14 | 0.08 | 0.16 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[4.75-5.25] | 5 | 9.07 | 413.83 | 257 | 0.06 | 0.37 | 0.37 | 4.99 | 9.7 | 438.87 | 135 | 0.36 | 0.61 | 0.71 | 4.99 | 10.6 | 457.79 | 264 | 0.24 | 0.93 | 0.96 | 5 | 10.09 | 445.63 | 204 | 0.28 | 0.65 | 0.71 | 5 | 12.88 | 498.68 | 110 | 0.56 | 1.31 | 1.42 | 4.98 | 15.44 | 538.91 | 94 | 0.7 | 1.7 | 1.84 | 4.99 | 12.4 | 485.17 | 94 | 0.6 | 0.91 | 1.09 | 4.98 | 8.17 | 385.32 | 23 | 1.12 | 0.88 | 1.43 | 5.08 | 2.05 | 215.62 | 6 | 0.48 | 0.38 | 0.62 | 5.11 | 1.16 | 173.4 | 1 | N/A | N/A | N/A
[5.25-5.75] | 5.48 | 11.97 | 467.56 | 195 | 0.09 | 0.48 | 0.49 | 5.5 | 13.86 | 518.41 | 97 | 0.5 | 1.46 | 1.54 | 5.49 | 14.21 | 525.44 | 188 | 0.34 | 1.29 | 1.34 | 5.52 | 14.96 | 536.76 | 145 | 0.43 | 1.69 | 1.75 | 5.49 | 17.02 | 567.25 | 79 | 0.72 | 1.5 | 1.66 | 5.47 | 16.93 | 566.28 | 59 | 0.82 | 0.66 | 1.05 | 5.48 | 15.7 | 544.43 | 54 | 0.84 | 1.22 | 1.48 | 5.48 | 11.5 | 467.98 | 16 | 1.33 | 1.2 | 1.8 | 5.28 | 8.19 | 403.6 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[5.75-6.25] | 5.99 | 15.58 | 526.26 | 173 | 0.11 | 0.61 | 0.62 | 5.96 | 18.18 | 585.79 | 62 | 0.85 | 1.8 | 1.99 | 5.98 | 18.34 | 587.59 | 160 | 0.54 | 1.66 | 1.74 | 6 | 18.37 | 589.29 | 121 | 0.55 | 1.4 | 1.5 | 6.01 | 21.68 | 640.23 | 54 | 0.74 | 1.79 | 1.94 | 5.97 | 25.68 | 675.97 | 31 | 2.24 | 3.32 | 4.01 | 6.01 | 20.85 | 621.87 | 33 | 1.36 | 1.91 | 2.34 | 5.95 | 13.33 | 506.16 | 5 | 2.24 | 0.79 | 2.37 | 5.92 | 6.5 | 362.95 | 2 | 1.59 | 0.52 | 1.67 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[6.25-6.75] | 6.5 | 19.86 | 590.79 | 128 | 0.16 | 0.77 | 0.79 | 6.47 | 24.55 | 673.36 | 41 | 1.14 | 2.63 | 2.87 | 6.49 | 22.74 | 650.82 | 103 | 0.79 | 1.84 | 2 | 6.49 | 22.59 | 649.41 | 95 | 0.72 | 1.83 | 1.97 | 6.51 | 27.04 | 703.44 | 33 | 1.34 | 2.26 | 2.62 | 6.51 | 32.94 | 765.23 | 22 | 2.4 | 2.84 | 3.71 | 6.56 | 31.28 | 748.75 | 11 | 3.18 | 3.97 | 5.09 | 6.53 | 14.37 | 529.85 | 2 | 2.88 | 0.51 | 2.93 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[6.75-7.25] | 7 | 24.41 | 652.58 | 77 | 0.21 | 0.94 | 0.97 | 7 | 26.84 | 701.64 | 34 | 1.24 | 1.12 | 1.67 | 7.03 | 29.11 | 728.5 | 95 | 0.89 | 2.7 | 2.84 | 6.98 | 30.52 | 747.72 | 68 | 0.93 | 3.64 | 3.76 | 7.02 | 31.98 | 763.09 | 32 | 1.24 | 2.29 | 2.61 | 7 | 35.46 | 797.06 | 13 | 3.09 | 1.39 | 3.39 | 6.96 | 36.71 | 805.05 | 14 | 3.65 | 3.11 | 4.79 | 7.01 | 22.36 | 652.3 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[7.25-7.75] | 7.48 | 29.65 | 717.45 | 81 | 0.31 | 1.14 | 1.18 | 7.47 | 35.61 | 802.29 | 24 | 1.82 | 4.45 | 4.81 | 7.47 | 34.73 | 792.24 | 66 | 1.05 | 3.14 | 3.31 | 7.5 | 36.75 | 814.11 | 50 | 1.18 | 2.95 | 3.18 | 7.53 | 39.92 | 849.66 | 14 | 1.59 | 3.8 | 4.12 | 7.48 | 38.58 | 832.92 | 6 | 4.19 | 1.74 | 4.54 | 7.33 | 37.86 | 824.65 | 4 | 4.19 | 1.08 | 4.33 | 7.71 | 51.75 | 963.5 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[7.75-8.25] | 8.01 | 35.65 | 782.09 | 86 | 0.29 | 1.36 | 1.39 | 7.9 | 42.13 | 865.07 | 20 | 2.11 | 3.9 | 4.43 | 7.97 | 42.1 | 864.23 | 36 | 1.9 | 3.81 | 4.25 | 8.02 | 41.75 | 856.5 | 27 | 2.93 | 2.61 | 3.93 | 7.86 | 45.67 | 901.9 | 3 | 3.62 | 4.38 | 5.68 | 8.02 | 44.48 | 880.97 | 3 | 9.44 | 2.92 | 9.88 | 7.89 | 54.05 | 977.9 | 2 | 7.76 | 7.39 | 10.72 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[8.25-8.75] | 8.23 | 38.77 | 812.88 | 95 | 0.31 | 1.48 | 1.51 | 8.57 | 39.93 | 845.59 | 8 | 3.93 | 1.24 | 4.12 | 8.49 | 47.68 | 916.17 | 19 | 2.72 | 3.04 | 4.08 | 8.49 | 46.49 | 903.33 | 23 | 2.72 | 2.88 | 3.96 | 8.55 | 54.22 | 975.38 | 4 | 4 | 3.55 | 5.35 | 8.56 | 62.1 | 1041.05 | 2 | 2.77 | 8.93 | 9.35 | 8.45 | 64.25 | 1059.3 | 2 | 4.29 | 5.05 | 6.62 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[8.75-9.25] | 8.76 | 45.96 | 881.7 | 64 | 0.43 | 1.75 | 1.8 | 8.89 | 42.51 | 870.13 | 3 | 5.7 | 2.42 | 6.19 | 9.02 | 48.09 | 917.11 | 11 | 4.13 | 1.04 | 4.26 | 8.96 | 50.4 | 936.45 | 6 | 6.89 | 2.59 | 7.36 | 9.01 | 64.83 | 1052.18 | 4 | 10.58 | 6.71 | 12.53 | 9.06 | 73.12 | 1124.6 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[9.25-9.75] | 9.23 | 52.39 | 937.37 | 75 | 0.41 | 1.99 | 2.03 | 9.61 | 47.68 | 919.8 | 1 | N/A | N/A | N/A | 9.48 | 59.45 | 1017.54 | 8 | 4.64 | 7.54 | 8.85 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 9.56 | 76.03 | 1147.2 | 2 | 1.6 | 6.38 | 6.58 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[9.75-10.25] | 9.76 | 62.39 | 1018.09 | 61 | 0.52 | 2.36 | 2.42 | 9.9 | 72.47 | 1116.83 | 3 | 8.1 | 85.5 | 85.88 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 9.99 | 57.19 | 992.95 | 4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[10.25-10.75] | 10.22 | 70.9 | 1081.07 | 67 | 0.5 | 2.68 | 2.73 | 10.63 | 102.42 | 1312.4 | 1 | N/A | N/A | N/A | 10.32 | 73.95 | 1126.2 | 1 | N/A | N/A | N/A | 10.6 | 86.19 | 1213.3 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[10.75-11.25] | 10.76 | 80.39 | 1145.58 | 34 | 0.72 | 3.04 | 3.12 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 10.99 | 97.42 | 1286.9 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[11.25-11.75] | 11.27 | 92.62 | 1227.44 | 22 | 1.07 | 3.5 | 3.66 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[11.75-12.25] | 11.79 | 103.34 | 1294.85 | 22 | 1.58 | 3.9 | 4.2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[12.25-12.75] | 12.26 | 112.23 | 1348 | 9 | 1.97 | 4.23 | 4.67 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[12.75-13.25] | 12.92 | 129.61 | 1454.03 | 2 | 1.59 | 4.88 | 5.13 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[13.25-13.75] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[13.75-14.25] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[14.25-14.75] | 14.03 | 158.61 | 1596.03 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Vi | average wind speed in bin i, in m/s
Pi | average wind turbine power output in bin i, in W
RPM | average wind turbine rotational speed in bin i, in revolutions per minute
Ni | number of 1-minute data sets in bin i
si | statistical uncertainty of the normalized and averaged power in bin i
ui | uncertainty in bin i related to the instruments used for the measurements
uci | combined uncertainty of the wind turbine power output in bin i